## ModBus-Definition 1.9
Address | Group | Ident | ScaleIdent | Description | Profile | VarType | Factor | Quantity | RFunction | WFunction | FWVersion
0 | Consumption | ConsFromAll |  | Home own consumption from all | ~Power | $VT_Float | 0 |  |  |  | 1.42
0 | SystemState | PMGridState |  | Grid state | Grid.State | $VT_UnsignedInteger | 0 |  |  |  | 1.42
0 | Battery | BTState |  | Battery state | Battery.State | $VT_UnsignedInteger | 0 |  |  |  | 1.42
0 | PV | PVPowerStrTot |  | Total DC Power from PV strings | ~Power | $VT_Float | 0 |  |  |  | 1.42
0 | Surplus | SPCharge |  | PV surplus battery charging |  | $VT_UnsignedInteger | 0 |  |  |  | 1.42
0 | Surplus | SPFeedin |  | PV surplus feed in |  | $VT_UnsignedInteger | 0 |  |  |  | 1.42
0 | Surplus | SPReduction |  | PV surplus reduction |  | $VT_UnsignedInteger | 0 |  |  |  | 1.42
2 | DeviceInfo | MBEnable |  | MODBUS Enable |  | $VT_Boolean | 1 | 1 | $FC_Read_HoldingRegisters | $FC_Write_SingleHoldingRegister | 1.44
4 | DeviceInfo | MBUnitID |  | MODBUS Unit-ID |  | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters | $FC_Write_SingleHoldingRegister | 1.44
5 | DeviceInfo | MBByteOrder |  | MODBUS Byte Order |  | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters | $FC_Write_SingleHoldingRegister | 1.44
6 | DeviceInfo | ArticleNr |  | Inverter article number |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
14 | DeviceInfo | SerialNr |  | Inverter serial number |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
30 | DeviceInfo | NumberConv |  | Number of bidirectional converter |  | $VT_UnsignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.42
32 | DeviceInfo | NumberACPhases |  | Number of AC phases |  | $VT_UnsignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.42
34 | DeviceInfo | NumberPVStrings |  | Number of PV strings |  | $VT_UnsignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.42
36 | DeviceInfo | HardwareVersion |  | Hardware-Version |  | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
38 | DeviceInfo | SoftwareVersionMC |  | Software-Version Maincontroller (MC) |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
46 | DeviceInfo | SoftwareVersionIOC |  | Software-Version IO-Controller (IOC) |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
54 | DeviceInfo | PowerID |  | Power-ID |  | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
56 | SystemState | InverterState |  | Inverter state | Status.KostalWR | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
100 | DeviceInfo | TotalDCPower |  | Total DC power | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
104 | SystemState | EnergyManagerState |  | State of energy manager | Status.KostalEM | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
106 | Consumption | ConsFromBT |  | Home own consumption from battery | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
108 | Consumption | ConsFromAC |  | Home own consumption from grid | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
110 | Consumption | ConsFromBTTot |  | Total home consumption Battery | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
112 | Consumption | ConsFromACTot |  | Total home consumption Grid | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
114 | Consumption | ConsFromPVTot |  | Total home consumption PV | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
116 | Consumption | ConsFromPV |  | Home own consumption from PV | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
118 | Consumption | ConsTot |  | Total home consumption | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
120 | PV | PVIsoResistance |  | Isolation resistance |  | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
122 | AC | ACLimitEVU |  | Power limit from EVU | Percent | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
124 | Consumption | ConsRate |  | Total home consumption rate | Percent | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
144 | SystemState | Worktime |  | Worktime |  | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
150 | AC | ACCosPhi |  | Actual cos φ |  | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
152 | AC | ACFrequency |  | Grid frequency | ~Hertz | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
154 | AC | ACCurrentP1 |  | Current Phase 1 | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
156 | AC | ACActivePowerP1 |  | Active power Phase 1 | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
158 | AC | ACVoltageP1 |  | Voltage Phase 1 | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
160 | AC | ACCurrentP2 |  | Current Phase 2 | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
162 | AC | ACActivePowerP2 |  | Active power Phase 2 | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
164 | AC | ACVoltageP2 |  | Voltage Phase 2 | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
166 | AC | ACCurrentP3 |  | Current Phase 3 | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
168 | AC | ACActivePowerP3 |  | Active power Phase 3 | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
170 | AC | ACVoltageP3 |  | Voltage Phase 3 | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
172 | AC | ACActivePowerTot |  | Total AC active power | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
174 | AC | ACReactivePowerTot |  | Total AC reactive power | Power.VaR | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
178 | AC | ACApparentPowerTot |  | Total AC apparent power | Power.VA | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
190 | BTInfo | BTmaxChargeCurrent |  | Max. Battery charge current | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.44
194 | Battery | BTCycles |  | Number of battery cycles |  | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
200 | Battery | BTCurrent |  | Actual battery charge (-) / discharge (+) current | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
202 | SystemState | FuseState |  | PSSB fuse state | Status.KostalFuse | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
208 | DeviceInfo | BTReadyFlag |  | Battery ready flag |  | $VT_Float | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
210 | Battery | BTCharge |  | Actual state of charge | Battery.Charge | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
214 | Battery | BTTemperature |  | Battery temperature | ~Temperature | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
216 | Battery | BTVoltage |  | Battery voltage | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
218 | Powermeter | PMCosPhi |  | Cos φ (powermeter) |  | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
220 | Powermeter | PMFrequency |  | Frequency (powermeter) | ~Hertz | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
222 | Powermeter | PMCurrentP1 |  | Current phase 1 (powermeter) | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
224 | Powermeter | PMActivePowerP1 |  | Active power phase 1 (powermeter) | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
226 | Powermeter | PMReactivePowerP1 |  | Reactive power phase 1 (powermeter) | Power.VaR | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
228 | Powermeter | PMApparentPowerP1 |  | Apparent power phase 1 (powermeter) | Power.VA | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
230 | Powermeter | PMVoltageP1 |  | Voltage phase 1 (powermeter) | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
232 | Powermeter | PMCurrentP2 |  | Current phase 2 (powermeter) | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
234 | Powermeter | PMActivePowerP2 |  | Active power phase 2 (powermeter) | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
236 | Powermeter | PMReactivePowerP2 |  | Reactive power phase 2 (powermeter) | Power.VaR | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
238 | Powermeter | PMApparentPowerP2 |  | Apparent power phase 2 (powermeter) | Power.VA | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
240 | Powermeter | PMVoltageP2 |  | Voltage phase 2 (powermeter) | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
242 | Powermeter | PMCurrentP3 |  | Current phase 3 (powermeter) | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
244 | Powermeter | PMActivePowerP3 |  | Active power phase 3 (powermeter) | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
246 | Powermeter | PMReactivePowerP3 |  | Reactive power phase 3 (powermeter) | Power.VaR | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
248 | Powermeter | PMApparentPowerP3 |  | Apparent power phase 3 (powermeter) | Power.VA | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
250 | Powermeter | PMVoltageP3 |  | Voltage phase 3 (powermeter) | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
252 | Powermeter | PMActivePowerTot |  | Total active power (powermeter) | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
254 | Powermeter | PMReactivePowerTot |  | Total reactive power (powermeter) | Power.VaR | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
256 | Powermeter | PMApparentPowerTot |  | Total apparent power (powermeter) | Power.VA | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
258 | PV | PVCurrentDC1 |  | Current DC1 | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
260 | PV | PVPowerDC1 |  | Power DC1 | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
266 | PV | PVVoltageDC1 |  | Voltage DC1 | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
268 | PV | PVCurrentDC2 |  | Current DC2 | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
270 | PV | PVPowerDC2 |  | Power DC2 | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
276 | PV | PVVoltageDC2 |  | Voltage DC2 | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
278 | PV | PVCurrentDC3 |  | Current DC3 | ~Ampere | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
280 | PV | PVPowerDC3 |  | Power DC3 | ~Power | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
286 | PV | PVVoltageDC3 |  | Voltage DC3 | ~Volt | $VT_Float | 1 | 2 | $FC_Read_HoldingRegisters |  | 1.42
320 | Yield | YieldTot |  | Total yield | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
322 | Yield | YieldDaily |  | Daily yield | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
324 | Yield | YieldYearly |  | Yearly yield | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
326 | Yield | YieldMonthly |  | Monthly yield | ~Electricity | $VT_Float | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
384 | DeviceInfo | NetworkName |  | Inverter network name |  | $VT_String | 0 | 32 | $FC_Read_HoldingRegisters |  | 1.42
416 | DeviceInfo | NetworkEnabled |  | IP enable |  | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.42
418 | DeviceInfo | NetworkAutoIP |  | Manual / Auto IP |  | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.42
420 | DeviceInfo | NetworkIP |  | IP-address |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
428 | DeviceInfo | NetworkMask |  | IP-subnetmask |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
436 | DeviceInfo | NetworkGW |  | IP-gateway |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
444 | DeviceInfo | NetworkAutoDNS |  | IP-auto-DNS |  | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.42
446 | DeviceInfo | NetworkDNS1 |  | IP-DNS1 |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
454 | DeviceInfo | NetworkDNS2 |  | IP-DNS2 |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
512 | BTInfo | BTCrossCapacity |  | Battery gross capacity | Battery.Capacity | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
514 | Battery | BTActualSOC |  | Battery actual SOC | Percent | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.42
515 | BTInfo | BTFirmwareMC |  | Battery Firmware Maincontroller (MC) |  | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
517 | BTInfo | BTManufacturer |  | Battery Manufacturer |  | $VT_String | 0 | 8 | $FC_Read_HoldingRegisters |  | 1.42
525 | BTInfo | BTModelID |  | Battery Model ID |  | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
527 | BTInfo | BTSerialNr |  | Battery Serial Number |  | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.42
529 | BTInfo | BTWorkCapacity |  | Battery work capacity | ~Electricity | $VT_UnsignedInteger | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
531 | DeviceInfo | MaxPower | SFMaxPower | Inverter Max Power | ~Power | $VT_UnsignedInteger | 0.001 | 1 | $FC_Read_HoldingRegisters |  | 1.42
532 | DeviceInfo | SFMaxPower |  | Inverter Max Power Scale Factor |  | $VT_SignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.44
533 | ACControl | ACCActivePower |  | Active Power Setpoint | Percent | $VT_UnsignedInteger | 0 | 1 |  | $FC_Write_SingleHoldingRegister | 1.44
535 | DeviceInfo | Manufacturer |  | Inverter Manufacturer |  | $VT_String | 0 | 16 | $FC_Read_HoldingRegisters |  | 1.42
559 | DeviceInfo | SerialNr1 |  | Inverter Serial Number |  | $VT_String | 0 | 16 | $FC_Read_HoldingRegisters |  | 1.42
575 | AC | ACInverterPower | ACSFInverterPower | Inverter Generation Power (actual) | ~Power | $VT_SignedInteger | 0.001 | 1 | $FC_Read_HoldingRegisters |  | 1.42
576 | AC | ACSFInverterPower |  | Power Scale Factor (Inverter Generation) |  | $VT_SignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.44
577 | AC | ACGenEnergy | ACSFGenEnergy | Inverter Generation Energy | ~Electricity | $VT_UnsignedInteger | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
579 | AC | ACSFGenEnergy |  | Energy Scale Factor (Inverter Generation) |  | $VT_SignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.44
582 | Battery | BTPower |  | Actual battery charge (-) / discharge (+) power | ~Power | $VT_SignedInteger | 0.001 | 1 | $FC_Read_HoldingRegisters |  | 1.42
583 | ACControl | ACCReactivePower |  | Reactive Power Setpoint | Percent | $VT_SignedInteger | 0 | 1 |  | $FC_Write_SingleHoldingRegister | 1.44
585 | ACControl | ACCCosPhi |  | Delta-cos φ Setpoint |  | $VT_SignedInteger | 0 | 1 |  | $FC_Write_SingleHoldingRegister | 1.44
586 | BTInfo | BTFirmware |  | Battery Firmware |  | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.42
588 | BTInfo | BTType |  | Battery Type | Battery.Type | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.42
768 | DeviceInfo | ProductName |  | Productname |  | $VT_String | 0 | 32 | $FC_Read_HoldingRegisters |  | 1.42
800 | DeviceInfo | PowerClass |  | Power class |  | $VT_String | 0 | 32 | $FC_Read_HoldingRegisters |  | 1.42
832 | ACControl | ACCLPActivePower | ACCSFLPActivePower | Low-Priority Active Power Setpoint | ~Power | $VT_UnsignedInteger | 1 | 1 |  | $FC_Write_SingleHoldingRegister | 1.44
833 | ACControl | ACCSFLPActivePower |  | Low-Priority Active Power Setpoint Scale Factor |  | $VT_SignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.44
1024 | BTControl | BTCACcPower | BTCSFACcPower | Battery charge power (AC) Setpoint | ~Power | $VT_SignedInteger | 0.001 | 1 |  | $FC_Write_SingleHoldingRegister | 1.44
1025 | BTControl | BTCSFACcPower |  | Power Scale Factor (Battery charge power AC) |  | $VT_SignedInteger | 1 | 1 | $FC_Read_HoldingRegisters |  | 1.44
1026 | BTControl | BTCACcPowerAbs |  | Battery charge power (AC) Setpoint (absolute) | ~Power | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1028 | BTControl | BTCDCcCurrentRel |  | Battery charge current (DC) Setpoint (relative) | Percent | $VT_Real | 1 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1030 | BTControl | BTCACcPowerRel |  | Battery charge power (AC) Setpoint (relative) | Percent | $VT_Real | 1 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1032 | BTControl | BTCDCcCurrentAbs |  | Battery charge current (DC) Setpoint (absolute) | ~Ampere | $VT_Real | 1 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1034 | BTControl | BTCDCcPowerAbs |  | Battery charge power (DC) Setpoint (absolute) | ~Power | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1036 | BTControl | BTCDCcPowerRel |  | Battery charge power (DC) Setpoint (relative) | Percent | $VT_Real | 1 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1038 | BTControl | BTCcPowerAbs |  | Battery max. charge power limit (absolute) | ~Power | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1040 | BTControl | BTCdPowerAbs |  | Battery max. discharge power limit (absolute) | ~Power | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1042 | BTControl | BTCminSOC |  | Minimum SOC | Percent | $VT_Real | 1 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1044 | BTControl | BTCmaxSOC |  | Maximum SOC | Percent | $VT_Real | 1 | 2 | $FC_Read_HoldingRegisters | $FC_Write_MultipleHoldingRegisters | 1.44
1046 | Battery | BTcEnergyDCTot |  | Total DC charge energy (DC-side to battery) | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1048 | Battery | BTdEnergyDCTot |  | Total DC discharge energy (DC-side from battery) | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1050 | Battery | BTcEnergyACTot |  | Total AC charge energy (AC-side to battery) | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1052 | Battery | BTdEnergyGridTot |  | Total AC discharge energy (battery to grid) | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1054 | Battery | BTcEnergyGridTot |  | Total AC charge energy (grid to battery) | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1056 | PV | PVEnergyTot |  | Total DC PV energy (sum of all PV inputs) | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1058 | PV | PVEnergyDC1 |  | Total DC energy from PV1 | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1060 | PV | PVEnergyDC2 |  | Total DC energy from PV2 | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1062 | PV | PVEnergyDC3 |  | Total DC energy from PV3 | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1064 | AC | ACEnergyToGridTot |  | Total energy AC-side to grid | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.42
1066 | PV | PVPowerTot |  | Total DC power (sum of all PV inputs) | ~Power | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1068 | BTInfo | BTWorkCapacity1 |  | Battery work capacity | ~Electricity | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1070 | BTInfo | BTSerialNr1 |  | Battery serial number |  | $VT_UnsignedInteger | 0 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1076 | BTControl | BTCcPowerMax |  | Maximum charge power limit (read-out from battery) | ~Power | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1078 | BTControl | BTCdPowerMax |  | Maximum discharge power limit (read-out from battery) | ~Power | $VT_Real | 0.001 | 2 | $FC_Read_HoldingRegisters |  | 1.44
1080 | BTControl | BTCMode |  | Battery management mode |  | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.44
1082 | DeviceInfo | SensorType |  | Installed Powermeter | Sensor.Type | $VT_UnsignedInteger | 0 | 1 | $FC_Read_HoldingRegisters |  | 1.44
Note on A1: 0 = Berechneter Wert